# HVAC

## Scope of Work

- This outline describes the requirements of an HVAC contract to provide a fully functioning, code compliant HVAC system which meets the requirements outlined herein. All work shall be subject to review by the Owner and Architect. This Narrative is intended to assist the Contractor in preparing his proposal. This Contractor shall include time to coordinate the systems selected with the energy model to meet the checklist requirements. Modifications to the system may be required to meet the checklist requirements.

- Existing air handling units and main ductwork distribution system shall be reused. Each unit shall have a variable air volume terminal unit with electric reheat, piping, ductwork, grilles and diffusers, controls, etc.

- The HVAC Contractor will complete all control wiring required under this section.

- Coordinate routing of ductwork with Architect, Construction Manager, building components and all other contractors.

- All ductwork to be held as high as possible and above ceilings.

- Coordinate with the Electrical Subcontractor for connection of equipment. Work includes, but is not limited to, submission of approved submittals to the Electrical Contractor for review of voltage, coordination of terminations, start-up, testing, trouble shooting, etc.

- Provide all hangers and supports, trapeze pipe hangers, thermal-hanger shield inserts, fittings, valves, anchors, coverings, equipment, vibration isolation, etc.

- Fire dampers, smoke dampers or combination fire / smoke dampers shall be provided as required by the OBC or the Authority Having Jurisdiction.

## Design Criteria

- This document describes the criteria for a high rise residential facility with a mixed use occupancy of commercial and living spaces.

- The building shall be designed in accordance with the following outdoor air conditions.

Summer dry / Wet bulb;	93 / 75 degrees F

Winter dry bulb;                              0   degrees F

- The building shall be designed in accordance with ASHRAE Standard 55-2023 and the following indoor conditions. If conflict shall occur between the provided values below and values recommended by ASHRAE Standard 55-2023, recommended values by ASHRAE Standard 55-2023 shall be used.

Summer	Winter

Commercial Spaces	74 F	72 F

Residences	74 F	72 F

Corridors	76 F	72 F

Stairwells	85 F	60 F

Mechanical Room	85 F	60 F

Storage Room	76 F	60 F

Elevator Equipment Rooms	85 F	60 F

Electric Rooms	85 F	60 F

- Load calculations for equipment sizing shall be sized in accordance with the procedures described in ASHRAE/ACCA Standard 183-2024.

  - Preliminary sizing of cooling equipment can be based on the following square foot per ton average. However, all final equipment sizing must be determined based on the previous mentioned guidelines.

    - Office/admin areas; 300-350 square foot/ton.

    - Densely occupied spaces (i.e., conference rooms, multi-purpose, lobby): 250-300 square foot/ton.

    - Restrooms/storage rooms: 350-400 square foot/ton.

    - Fitness room: 150-250 square foot/ton.

    - Future retail / restaurant tenant spaces: 150-250 square foot/ton

- Building load calculations shall be based on the floor plans, elevations, wall sections, details, etc., as indicated on the architectural plans.

- Equipment acoustics ratings shall comply with ASHRAE.

- Outdoor air ventilation is existing ducted to main air handling unit.

- Coordination

- Coordinate all matters relating to the physical location of equipment, ductwork, grilles, registers, diffusers and any other devices with the Construction Manager and all other trades. Coordinate all aspects of the design and installation with civil, structural, architectural and electrical systems.

## Room HVAC Systems

- Dwelling units shall have an individual, horizontal, variable air volume unit located above ceiling with ducted supply within the dwelling unit. Return shall be ducted to the air handling unit.

- Residential kitchen hood shall be recirculating type on the 14th floor. All other floors shall be a recirculating microwave over the range.

- The Lobby, Retail Area, Offices, Lounge, Leasing Office, and all corridors shall be provided with a variable air volume terminal unit with electric reheat coil, wired, and diffusers. Return is ducted to the air handling unit. Units to be located above the ceiling.

- The air distribution system shall be fully ducted supply and return; with insulation wrap on the supply ductwork and internal acoustic lining on the return ductwork. Provide an easily accessible filter box, housing a common filter size for all terminal units. Ductwork shall be per SMACNA requirements and sealed to prevent air leakage.

- Stairwells, Mechanical Equipment Rooms, Electrical Rooms and Storage Rooms shall not be air conditioned. Electrical rooms shall be exhausted.

- The thermostats shall be low voltage, programmable controls with heat / cool compatible with building automation system. The units shall have night setback capabilities. Thermostat location shall be determined by Construction Manager / Architect.

- Dryers are ventless.

## General Fan / Exhaust Systems

- Individual dwelling unit bathrooms shall utilize dual speed residential toilet exhaust fans, separately controlled by Electrical Contractor for continuous exhaust. Individual exhaust ducts shall be extended to a riser to the roof. Fan shall be at the top of the exhaust stack to maintain building pressurization.

- All exhaust outlets must be coordinated with intakes for clearance by code.

- For the garage provide an exhaust system to provide ventilation per the Ohio Building Code. Provide a carbon monoxide monitoring system to activate the exhaust system to full flow whenever an unsafe level of CO is reached.

## Accessory Equipment and Materials

- Cabinet Heaters: Electric cabinet heaters shall be QMark, Berko, Redd-I or approved equal. Heaters shall be controlled by a line voltage thermostat. Locate near exterior entrance doors. Size for infiltration of 9 cfm / sq. ft. of door area and a 65 degree temperature difference. Locate two (2) in each stairwell.

- Diffusers, Grilles, and Registers

  - Air devices shall be furnished and installed by this Contractor.

  - Supply registers/grilles: Steel, dual deflection, equal to Titus Model 300 FS.

  - Return registers/grilles: Steel, single deflection, equal to Titus Model 350 RL.

  - Ceiling diffusers:	Ceiling diffuser equal to Titus Model OMNI shall be installed in gypsum board ceilings. Diffusers shall have a fire rated damper for installation in a fire rated ceiling floor assembly.

- Dampers: Provide volume dampers and UL fire / smoke dampers for NFPA 90A of size as required for balancing or to maintain fire separation rating of system through which	ductwork is to pass. Manufacturer shall be equal to Louvers and Dampers, Aerolite, Prefco and Ruskin.

- Access panels are to be provided under this subcontract where required by code and where maintenance duties would make practical, lockable UL listed access panels for equipment and piping concealed in walls, floor or ceilings will be a minimum of 12"x12" and of proper fire rating to maintain surrounding structure.

## Ductwork

- All ductwork shall be provided per SMACNA “HVAC Duct Construction Standards – Metal and Flexible”. All ductwork shall have sealants that are low-emitting adhesives and sealants according to LEED requirements. Ductwork leakage rate shall be a maximum 5%.

- Flexible ductwork shall be routed from main distribution duct to diffusers in rooms.

- Size all ductwork according to the following parameters:

- Low pressure supply ductwork: 0.08-0.1” per 100 feet of duct.

- Exhaust ductwork: 0.08-0.1” per 100 feet of duct.

- Return ductwork: 0.05-0.08” per 100 feet of duct.

- Furnish and install neoprene flexible duct connections at the inlet of terminal units and fans.

- Furnish and install opposed-blade, multi-leaf, leak-proof volume control dampers at locations in supply, return and exhaust ducts where branches are taken from larger ducts and as required to achieve system air balance quantities. Balancing devices must be provided in accordance with Section 603.17 of the Ohio Mechanical Code.

- Testing, Balancing, and Adjusting shall be the responsibility of this Contractor.

- The individual performing the air balancing shall be a certified Test and Balance Contractor and a member of NEBB or AABC. Recently calibrated equipment must be used. The certified air balancer shall accurately balance the systems to provide air quantities as indicated on the design/build drawings and schedules/specifications, operate automatic control systems and verify set points during balancing. Air Balance Contractor shall comply with ASHRAE instrumentation, air balancing, system balancing requirements and reporting.

- Provide written reports to the Construction Manager for review, prior to Certificate of Occupancy.

## Hangers and Supports

- Support all ductwork and equipment by hangers or brackets. Furnish structural steel members where required to support equipment. No portion of ductwork shall be supported by equipment, piping, ceilings, etc.

- Support ductwork by means of hangers as follows:

Duct Width	Hanger Size and Type	Max. Spacing

| 60 or less | 1"x.109" (#12 gage) | 8 feet |
| --- | --- | --- |
| 61 to 90 | 3/8" dia. rod | 8 feet |

- A pair of hangers shall be located at every transverse joint and elsewhere according to the table.

- Provide sleeves at wall, floor and foundation penetrations where required by Code and good practice. Maintain fire separation by use of caulk, grout or other UL rated systems. Maintain watertight installation where required. Provide escutcheons (chrome) where exposed.

## Mechanical Insulation

- Ductwork Insulation Materials:

- Flexible Fiberglass Ductwork Insulation: Glass fibers bonded with a thermosetting resin. Comply with ASTM C 553, Type II, without facing and with vapor barrier all-service jacket manufactured from kraft paper, reinforcing scrim, aluminum foil and vinyl film.

- Vapor Barrier Material for Ductwork: Paper-backed aluminum-foil, except as otherwise indicated; strength and permeability rating equivalent to factory-applied vapor barriers on adjoining ductwork insulation, where available.

- Ductwork Insulation Accessories: Provide staples, bands, wires, tape, anchors, corner angles and similar accessories as recommended by insulation manufacturer for applications indicated.

- Ductwork Insulation Compounds: Provide cements, adhesives, coatings, sealers, protective finishes and similar compounds as recommended by insulation manufacturer for applications indicated.

- Cold Ductwork System Insulation (below ambient temperature). Insulation shall comply with ASHRAE 90.1-2007.

- HVAC supply ductwork between fan discharge or HVAC unit discharge and room terminal outlet.

- HVAC ductwork three (3) feet downstream of roof penetrations.

- HVAC louvers, plenums and ductwork three (3) feet downstream of wall penetrations.

- Insulate each ductwork system specified above with one of the following types and thicknesses of insulation:

- Externally wrapped flexible fiberglass; thickness to meet ASHRAE 90.1 energy code and LEED requirements, application limited to concealed locations.

- Internally lined flexible fiberglass, ½” thick, application limited to return ductwork in dwelling units.

## Variable Air Volume Terminal Units

- Provide factory-assembled and tested, single duct variable air volume terminal units with factory mounted electric reheat coils. Units to be mounted above the ceiling.

- Electric reheat coils shall have SCR controllers.

- HVAC contractor shall install terminal units with adequate space for maintenance.

- Filters shall be replaced just prior to Owner’s occupancy.

- Variable Volume Terminal Units shall be equal to the following:

  - Price.

  - Titus.

  - Kruger.

  - Nailor.

  - Trane (The) Co.

## Fans

- Provide centrifugal ceiling exhausters, roof exhausters or utility sets all with AMCA Certified Ratings Seal. All roof fans shall require a roof curb provided by the HVAC Contractor.

- For bathroom exhaust fans, provide galvanized steel housing, lined with acoustical insulation, adaptable for ceiling or wall installation, centrifugal fan wheels mounted on motor shaft with fan shrouds all removable for service and integral back-draft damper fan discharge. Include steel louvered grille with flange on intake with thumbscrew attachment to fan housing. Motor shall be permanent split-capacitor motor, permanently lubricated. Toilet exhaust fans for living spaces shall meet an NC 40 (Maximum sones of 1.0 and / or 40 dBA) at the ceiling inlet grille.

- For rooftop exhaust fans, provide centrifugal power roof ventilators. Fan air flow baffle and removable top cap shall be spun aluminum. Fan base and integral curb cap shall be aluminum with welded corners. Fan wheel shall be aluminum with welded blades. Fan shall be belt-drive with cast iron pillow block bearings. Provide standard conduit through fan base into motor compartment.

- For each fan, provide either balanced backdraft or motor operated dampers interlocked with associated fan.

- Coordinate fan controls with the Electrical Contractor.

- Manufacturer: Fans to be equal to the following:

  - Cook Co., Loren

  - Greenheck.

  - Twin City Fan & Blower

## Stairway Pressurization/Atrium Smoke Exhaust System

- The stairways have an existing pressurization system and the Atrium has an existing smoke evacuation system which shall remain.